## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Executive Engineer, AIIMS Rishikesh
Name of Work: Designing, Planning and SITC of Cable Laying for Fountains, Submersible and Street Lights at AIIMS Rishikesh
NIT No: EW-MNTC/25/2020-215
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE including GST In Figures To be entered by the Bidder in Rs. P | Excise Duty | GST in % | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT with taxes | TOTAL AMOUNT with Taxes In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 5 | 14 | 6 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Providing of Aluminium conductor XLPE Insulated sheath Cable of 1.1 KV Grade conforming to IS : 1554 3.5 X 120 Sq. mm | item1 | 800 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
2 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 95 sq. mm and upto 185 sq. mm | item2 | 200 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
3 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | item3 | 300 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
4 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting,jointing etc. in the existing trench, complete as required. 120 mm dia (OD-120 mm & ID-103 mm nominal) | item4 | 150 | Meter |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
5 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 120 sq. mm (45mm) | item5 | 12 | Each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
6 | Supply and Fixing INDOOR/OUTDOOR PDB PANEL 1 incommer power supply and 2 Outgoing power supply. A) Main Incomer Panel Name : INDOOR/OUTDOOR PDB PANEL , Outdoor Power Distribution Panel with 450mm Stand Height ,400A FP 36KA MCCB With TMD Based Release. (DN3B - 400D ),Rotary Handle Mechanism, Spreader Links with Phase Barriers,Digital VAF Meter ,Ct's 400/5A, 15 VA, Cl-1'0, Tape Wound Type,Ct's Shorting Link,SP 6A Control MCB, 10 KA "C" Curve,Phase Indication Lamp Red , Yellow & Blue LED Type 220V AC ,Neutral Link . B) Outgoing Supply 250A FP MCCB -, 250A FP 36KA MCCB With TMD Based Release. ( DN2- 250D ),Rotary Handle Mechanism ,Spreader Links with Phase Barriers,1C/O + TAC Block ,On, Off, & Trip Indicator Lamp LED Type , SP 6A Control MCB, 10 KA "C" Curve , Neutral Link. C) Outgoing Supply 200A FP MCCB - , 200A FP 36KA MCCB With TMD Based Release. ( DN2- 250D ),Rotary Handle Mechanism , Spreader Links with Phase Barriers, 1C/O + TAC Block , On, Off, & Trip Indicator Lamp LED Type , SP 6A Control MCB, 10 KA "C" Curve , Neutral Link. PANEL BODY & BUS BAR SPECIFICATIONS Powder Coated Enclosure made of M.S sheet having 1.6mm thk. for load bearing surfaces & 1.2mm thk. for non load bearing surfaces,powder coated having Siemens grey color with HINDALCO/VALCO Make Alu. Busbar with support, PVC sleeve, hardware, power & control wiring etc. ALUMINIUM BUSBAR OF SIZES THE FOLLOWING. Size: 40mm x 10mm x 1 Nos Per Phase or equelant size, Size: 40mm x 5mm x 1 Nos for Neutral or equelant size, Size: 30mm x 5mm x 1 Nos for Earth, L - 1100 X D - 350 X H -1175mm | item6 | 2 | Nos. |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
7 | Electrical Panel Change Over 200A Outdoor Change Over Panel , Size - 1000x400x350mm With 450mm Height of Stand,200A Aluminum Busbar of C/O input & output for Cable Termination with color Coated PVC Sleeve Hardware . Busbar Size- 25x10mm each Phase & 25x5mm for Neutral , 200A FP On Load Change Over Switch. PANEL BODY & BUS BAR SPECIFICATIONS Powder Coated Enclosure made of M.S sheet having 1.6mm thk. for load bearing surfaces & 1.2mm thk. for non load bearing surfaces, powder coated having Siemens grey colour with HINDALCO/VALCO Make Alu. Busbar with support, PVC sleeve, hardware, power & control wiring etc. ALUMINIUM BUSBAR OF SIZE THE FOLLOWING 25x10mm each Phase & 25x5mm for Neutral. | item7 | 2 | Nos. | [5 empty] | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only
Total in Figures | [51 empty] | 0 | 0 |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information